## results
dataset | total_duration_years | mean_power_w | filtering_result | degradation_rate_pct_per_year | rate_reliable | unreliable_because | missing_maps | multiple_matches | statistical_trend_method | detected_or_created_columns | why_missing
multiyear1.csv | 8.684 | 48357.8 | 9.7% retained (330/3386 rows) | -0.4964 | yes |  | none | DC Power: dc_power__1136 (used), dc_power__1136, inv1_dc_power__1134, inv2_dc_power__1135 ¦ DC Voltage: inv2_dc_voltage__1048 (used), inv1_dc_voltage__1044, inv2_dc_voltage__1048 ¦ DC Current: inv2_dc_current__1049 (used), inv1_dc_current__1045, inv2_dc_current__1049 ¦ Irradiance: poa_irradiance_refcell__1054 (used), poa_irradiance__1055, poa_irradiance_refcell__1054 ¦ Module temperature: module_temp__1056 (used), module_temp__1056 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__1136 ¦ DC Voltage=inv2_dc_voltage__1048 ¦ DC Current=inv2_dc_current__1049 ¦ Irradiance=poa_irradiance_refcell__1054 ¦ Module temperature=module_temp__1056
multiyear2.csv | 9.859 | 5547.3 | 3.8% retained (137/3589 rows) | -0.2829 | yes |  | none | DC Power: dc_power_hw__2694 (used), dc_power_hw__2694, power_factor_1000__2693 ¦ DC Voltage: dc_voltage__2682 (used), dc_voltage__2682 ¦ DC Current: dc_current__2683 (used), dc_current__2683 ¦ Irradiance: poa_irradiance__2679 (used), poa_irradiance__2679 ¦ Module temperature: module_temp_f__2689 (used), module_temp_f__2689 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power_hw__2694 ¦ DC Voltage=dc_voltage__2682 ¦ DC Current=dc_current__2683 ¦ Irradiance=poa_irradiance__2679 ¦ Module temperature=module_temp_f__2689
multiyear3.csv | 15.422 | 175.6 | 15.7% retained (558/3559 rows) | -0.5613 | yes |  | none | DC Power: dc_power__314 (used), dc_power__314, dc_power__3971, power_factor__327, power_factor__3983, power_factor__3653 ¦ DC Voltage: dc_pos_voltage__316 (used), dc_pos_voltage__316, dc_voltage__3972, inv1_string1_dc_voltage__3627 ¦ DC Current: dc_pos_current__317 (used), dc_pos_current__317, dc_current__3973, inv1_string1_dc_current__3614 ¦ Irradiance: poa_irradiance__313 (used), poa_irradiance__313, poa_irradiance__3970, poa_irradiance__3604, intsolirrad__16, licor1_irradiance__3605, licor2_irradiance__3606, licor3_irradiance__3607, licor4_irradiance__3608, licor5_irradiance__3609, referencemodule1_irradiance__3610, referencemodule2_irradiance__3612 ¦ Module temperature: module_temp_1__321 (used), module_temp_1__321, mod_temperature__3974, module_temp_1__3658 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__314 ¦ DC Voltage=dc_pos_voltage__316 ¦ DC Current=dc_pos_current__317 ¦ Irradiance=poa_irradiance__313 ¦ Module temperature=module_temp_1__321
multiyear_compute_power_VxI_sys1429.csv | 1.673 | 711.4 | 22.5% retained (786/3499 rows) | -0.8076 | no | the data spans only 1.7 year(s) — under 2 years is too short to separate real aging from seasonal weather | none | DC Voltage: inv2_dc_voltage__4918 (used), inv1_dc_voltage__4912, inv2_dc_voltage__4918 ¦ DC Current: inv1_dc_current1__4913 (used), inv1_dc_current1__4913, inv1_dc_current2__4914, inv2_dc_current1__4919 ¦ Irradiance: poa_irradiance__4924 (used), poa_irradiance__4924, poa_irradiance_refcell1__4925, poa_irradiance_refcell2__4926 ¦ Module temperature: module_temp_1__4928 (used), module_temp_1__4928, module_temp_2__4929, module_temp_3__4930 | LR | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=inv2_dc_voltage__4918 ¦ DC Current=inv1_dc_current1__4913 ¦ Irradiance=poa_irradiance__4924 ¦ Module temperature=module_temp_1__4928
multiyear_full_dcnaming_sys3.csv | 7.009 | -802.2 | 12.3% retained (243/1981 rows) | -1.7994 | no | the year-over-year changes disagree with each other by about ±2.8%/yr — too scattered for this single number to be trusted | none | DC Power: dc_power__353 (used), dc_power__353 ¦ DC Voltage: dc_pos_voltage__354 (used), dc_pos_voltage__354 ¦ DC Current: dc_pos_current__355 (used), dc_pos_current__355 ¦ Irradiance: poa_irradiance__352 (used), poa_irradiance__352 ¦ Module temperature: module_temp_1__356 (used), module_temp_1__356 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__353 ¦ DC Voltage=dc_pos_voltage__354 ¦ DC Current=dc_pos_current__355 ¦ Irradiance=poa_irradiance__352 ¦ Module temperature=module_temp_1__356
multiyear_no_irradiance_sys1199.csv | 10.103 | 14534.9 | 45.0% retained (892/1983 rows) | 2.4735 | no | the computed rate (+2.5%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance | DC Power: dc_power__2715 (used), dc_power__2715, inv1_dc_power__2717, inv2_dc_power__2722, inv3_dc_power__2727, inv4_dc_power__2732, inv5_dc_power__2737, inv6_dc_power__2742, inv7_dc_power__2747 ¦ DC Voltage: inv1_dc_voltage__2718 (used), inv1_dc_voltage__2718, inv2_dc_voltage__2723, inv3_dc_voltage__2728 ¦ DC Current: inv1_dc_current__2719 (used), inv1_dc_current__2719, inv2_dc_current__2724, inv3_dc_current__2729 ¦ Module temperature: inv1_temp__2720 (used), inv1_temp__2720, inv2_temp__2725, inv3_temp__2730 | YOY | Time=measured_on ¦ DC Power=dc_power__2715 ¦ DC Voltage=inv1_dc_voltage__2718 ¦ DC Current=inv1_dc_current__2719 ¦ Module temperature=inv1_temp__2720
multiyear_power_only_sys1265.csv | 3.537 | 251.5 | 0.0% retained (0/3596 rows) |  |  |  | Module temperature | DC Power: ppv_avg__3430 (used), ppv_avg__3430 ¦ DC Current: a_avg__3431 (used), a_avg__3431 ¦ Irradiance: wh_sum__3428 (used), wh_sum__3428 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3430 ¦ DC Voltage=computed_dc_voltage ¦ DC Current=a_avg__3431 ¦ Irradiance=wh_sum__3428 | No degradation rate (stopped at 'filter'): Only 0 row(s) survived filtering (need >= 20) -- not enough clean data to estimate degradation. Correctly refused rather than guessing.
my_01_csv_10.csv | 22.582 | 228.8 | 21.0% retained (292/1393 rows) | -0.1619 | yes |  | none | DC Power: dc_power__422 (used), dc_power__422 ¦ DC Voltage: dc_pos_voltage__424 (used), dc_pos_voltage__424 ¦ DC Current: dc_pos_current__425 (used), dc_pos_current__425 ¦ Irradiance: poa_irradiance__421 (used), poa_irradiance__421 ¦ Module temperature: module_temp_1__429 (used), module_temp_1__429 | LR | Time=measured_on ¦ DC Power=dc_power__422 ¦ DC Voltage=dc_pos_voltage__424 ¦ DC Current=dc_pos_current__425 ¦ Irradiance=poa_irradiance__421 ¦ Module temperature=module_temp_1__429
my_02_csv_1199.csv | 10.001 | 14929.2 | 44.4% retained (347/782 rows) | 0.2011 | yes |  | Irradiance, Module temperature | DC Power: dc_power__2715 (used), dc_power__2715 ¦ DC Voltage: inv1_dc_voltage__2718 (used), inv1_dc_voltage__2718 ¦ DC Current: inv1_dc_current__2719 (used), inv1_dc_current__2719 | YOY | Time=measured_on ¦ DC Power=dc_power__2715 ¦ DC Voltage=inv1_dc_voltage__2718 ¦ DC Current=inv1_dc_current__2719
my_03_csv_1201.csv | 9.347 | 3918.6 | 7.6% retained (108/1429 rows) | 23.1772 | no | only 5 daily data point(s) survived filtering (a reliable trend needs at least 20); the computed rate (+23.2%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance, Module temperature | DC Power: dc_power_hw__2800 (used), dc_power_hw__2800 ¦ DC Voltage: dc_voltage__2795 (used), dc_voltage__2795 ¦ DC Current: dc_current__2796 (used), dc_current__2796 ¦ Irradiance: poa_irradiance__2789 | LR | Time=measured_on ¦ DC Power=dc_power_hw__2800 ¦ DC Voltage=dc_voltage__2795 ¦ DC Current=dc_current__2796
my_04_csv_1203.csv | 9.32 | 28500.7 | 23.5% retained (336/1431 rows) | -1.0459 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: dc_power__2890 (used), dc_power__2890 | LR | Time=measured_on ¦ DC Power=dc_power__2890
my_05_csv_1204.csv | 7.023 | 21160.4 | 6.8% retained (53/784 rows) | -2.024 | no | only 7 daily data point(s) survived filtering (a reliable trend needs at least 20) | none | DC Power: meas_pwr (used), meas_pwr ¦ DC Voltage: vdc1 (used), vdc1 ¦ DC Current: idc1 (used), idc1 ¦ Irradiance: g1 (used), g1 ¦ Module temperature: tm1 (used), tm1 | YOY | Time=measured_on ¦ DC Power=meas_pwr ¦ DC Voltage=vdc1 ¦ DC Current=idc1 ¦ Irradiance=g1 ¦ Module temperature=tm1
my_06_csv_1208.csv | 9.714 | 300099 | 22.3% retained (310/1391 rows) | -3.2929 | no | the computed rate (-3.3%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: val_power (used), val_power | YOY | Time=measured_on ¦ DC Power=val_power
my_07_csv_1214.csv | 3.693 | 211.5 | 99.4% retained (1414/1423 rows) | -0.0962 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3184 (used), ppv_avg__3184 ¦ DC Current: a_avg__3185 (used), a_avg__3185 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3184 ¦ DC Current=a_avg__3185
my_08_csv_1217.csv | 3.693 | 210.1 | 98.5% retained (1399/1421 rows) | -0.0621 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3265 (used), ppv_avg__3265 ¦ DC Current: a_avg__3266 (used), a_avg__3266 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3265 ¦ DC Current=a_avg__3266
my_09_csv_1219.csv | 3.693 | 207.9 | 98.2% retained (1395/1421 rows) | -0.0427 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3282 (used), ppv_avg__3282 ¦ DC Current: a_avg__3283 (used), a_avg__3283 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3282 ¦ DC Current=a_avg__3283
my_100_csv_1334.csv | 3.359 | 856.1 | 0.8% retained (27/3586 rows) | 0.0305 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: w_n_avg__3469 (used), w_n_avg__3469 ¦ Irradiance: wh_n_sum__3468 (used), wh_n_sum__3468 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=w_n_avg__3469 ¦ Irradiance=wh_n_sum__3468
my_101_csv_1403.csv | 5.476 | 1036.6 | 12.2% retained (436/3572 rows) | -2.7995 | yes |  | none | DC Power: dc_power__5033 (used), dc_power__5033 ¦ DC Voltage: inv1_dc_voltage__4202 (used), inv1_dc_voltage__4202, inv2_dc_voltage__4208 ¦ DC Current: inv1_dc_current1__4203 (used), inv1_dc_current1__4203, inv1_dc_current2__4204, inv2_dc_current1__4209 ¦ Irradiance: poa_irradiance__4214 (used), poa_irradiance__4214, poa_irradiance_refcell1__4215, poa_irradiance_refcell2__4216 ¦ Module temperature: module_temp_2__4219 (used), module_temp_1__4218, module_temp_2__4219, module_temp_3__4220 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__5033 ¦ DC Voltage=inv1_dc_voltage__4202 ¦ DC Current=inv1_dc_current1__4203 ¦ Irradiance=poa_irradiance__4214 ¦ Module temperature=module_temp_2__4219
my_102_csv_1420.csv | 4.901 | 387.4 | 13.9% retained (500/3600 rows) | -2.2083 | yes |  | none | DC Power: dc_power__5144 (used), dc_power__5144 ¦ DC Voltage: dc_voltage_vdc__4814 (used), dc_voltage_vdc__4814 ¦ DC Current: dc_current_i2__4815 (used), dc_current_i2__4815 ¦ Irradiance: poa_irradiance_sun__4810 (used), poa_irradiance_sun__4810 ¦ Module temperature: module_temp_f_temp1__4811 (used), module_temp_f_temp1__4811 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__5144 ¦ DC Voltage=dc_voltage_vdc__4814 ¦ DC Current=dc_current_i2__4815 ¦ Irradiance=poa_irradiance_sun__4810 ¦ Module temperature=module_temp_f_temp1__4811
my_103_csv_1422.csv | 3.179 | 425.1 | 4.9% retained (173/3516 rows) | -14.2044 | no | the computed rate (-14.2%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | none | DC Voltage: inv2_dc_voltage__4831 (used), inv1_dc_voltage__4825, inv2_dc_voltage__4831 ¦ DC Current: inv2_dc_current1__4832 (used), inv1_dc_current1__4826, inv1_dc_current2__4827, inv2_dc_current1__4832 ¦ Irradiance: poa_irradiance_refcell1__4838 (used), poa_irradiance__4837, poa_irradiance_refcell1__4838, poa_irradiance_refcell2__4839 ¦ Module temperature: module_temp_1__4841 (used), module_temp_1__4841, module_temp_2__4842, module_temp_3__4843 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=inv2_dc_voltage__4831 ¦ DC Current=inv2_dc_current1__4832 ¦ Irradiance=poa_irradiance_refcell1__4838 ¦ Module temperature=module_temp_1__4841
my_104_csv_1423.csv | 7.247 | 690.4 | 25.7% retained (899/3494 rows) | -0.8432 | yes |  | none | DC Voltage: inv2_dc_voltage__4855 (used), inv1_dc_voltage__4849, inv2_dc_voltage__4855 ¦ DC Current: inv1_dc_current2__4851 (used), inv1_dc_current1__4850, inv1_dc_current2__4851, inv2_dc_current1__4856 ¦ Irradiance: poa_irradiance__4861 (used), poa_irradiance__4861, poa_irradiance_refcell1__4862, poa_irradiance_refcell2__4863 ¦ Module temperature: module_temp_3__4867 (used), module_temp_1__4865, module_temp_2__4866, module_temp_3__4867 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=inv2_dc_voltage__4855 ¦ DC Current=inv1_dc_current2__4851 ¦ Irradiance=poa_irradiance__4861 ¦ Module temperature=module_temp_3__4867
my_105_csv_1429.csv | 1.673 | 711.4 | 22.5% retained (786/3499 rows) | -0.8076 | no | the data spans only 1.7 year(s) — under 2 years is too short to separate real aging from seasonal weather | none | DC Voltage: inv2_dc_voltage__4918 (used), inv1_dc_voltage__4912, inv2_dc_voltage__4918 ¦ DC Current: inv1_dc_current1__4913 (used), inv1_dc_current1__4913, inv1_dc_current2__4914, inv2_dc_current1__4919 ¦ Irradiance: poa_irradiance__4924 (used), poa_irradiance__4924, poa_irradiance_refcell1__4925, poa_irradiance_refcell2__4926 ¦ Module temperature: module_temp_1__4928 (used), module_temp_1__4928, module_temp_2__4929, module_temp_3__4930 | LR | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=inv2_dc_voltage__4918 ¦ DC Current=inv1_dc_current1__4913 ¦ Irradiance=poa_irradiance__4924 ¦ Module temperature=module_temp_1__4928
my_106_csv_2.csv | 9.947 | 21.4 | 17.6% retained (584/3309 rows) | 0.6575 | no | the computed rate (+0.7%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr); the year-over-year changes disagree with each other by about ±2.4%/yr — too scattered for this single number to be trusted | none | DC Power: dc_power__346 (used), dc_power__346 ¦ DC Voltage: dc_pos_voltage__347 (used), dc_pos_voltage__347 ¦ DC Current: dc_pos_current__348 (used), dc_pos_current__348 ¦ Irradiance: poa_irradiance__345 (used), poa_irradiance__345 ¦ Module temperature: module_temp_1__349 (used), module_temp_1__349 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__346 ¦ DC Voltage=dc_pos_voltage__347 ¦ DC Current=dc_pos_current__348 ¦ Irradiance=poa_irradiance__345 ¦ Module temperature=module_temp_1__349
my_107_csv_3.csv | 7.009 | -802.2 | 12.3% retained (243/1981 rows) | -1.7994 | no | the year-over-year changes disagree with each other by about ±2.8%/yr — too scattered for this single number to be trusted | none | DC Power: dc_power__353 (used), dc_power__353 ¦ DC Voltage: dc_pos_voltage__354 (used), dc_pos_voltage__354 ¦ DC Current: dc_pos_current__355 (used), dc_pos_current__355 ¦ Irradiance: poa_irradiance__352 (used), poa_irradiance__352 ¦ Module temperature: module_temp_1__356 (used), module_temp_1__356 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__353 ¦ DC Voltage=dc_pos_voltage__354 ¦ DC Current=dc_pos_current__355 ¦ Irradiance=poa_irradiance__352 ¦ Module temperature=module_temp_1__356
my_108_csv_33.csv | 12.241 | 428.4 | 16.9% retained (599/3554 rows) | -0.5192 | yes |  | none | DC Power: dc_power__583 (used), dc_power__583, dc_power__1136, dc_power__246, power_factor__596, inv1_dc_power__1134, inv2_dc_power__1135, dc_power__1084, power_factor__1097 ¦ DC Voltage: dc_pos_voltage__585 (used), dc_pos_voltage__585, inv1_dc_voltage__1044, inv2_dc_voltage__1048 ¦ DC Current: dc_pos_current__586 (used), dc_pos_current__586, inv1_dc_current__1045, inv2_dc_current__1049 ¦ Irradiance: poa_irradiance__582 (used), poa_irradiance__582, poa_irradiance__1055, poa_irradiance_refcell__1054, poa_irradiance__245, poa_irradiance__1083 ¦ Module temperature: module_temp_3__592 (used), module_temp_1__590, module_temp_2__591, module_temp_3__592 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__583 ¦ DC Voltage=dc_pos_voltage__585 ¦ DC Current=dc_pos_current__586 ¦ Irradiance=poa_irradiance__582 ¦ Module temperature=module_temp_3__592
my_109_csv_36.csv | 7.51 | 319.6 | 0.9% retained (32/3515 rows) | 6.8914 | no | the computed rate (+6.9%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr); the year-over-year changes disagree with each other by about ±44.0%/yr — too scattered for this single number to be trusted | none | DC Power: dc_power__628 (used), dc_power__628, dc_power__246, dc_power__374, dc_power__1084, power_factor__387, power_factor__1097 ¦ DC Voltage: dc_voltage__630 (used), dc_voltage__630, dc_pos_voltage__248, dc_pos_voltage__376, dc_pos_voltage__1086 ¦ DC Current: dc_current__631 (used), dc_current__631, dc_pos_current__249, dc_pos_current__377, dc_pos_current__1087 ¦ Irradiance: poa_irradiance_2__658 (used), poa_irradiance_1__627, poa_irradiance_2__658, poa_irradiance__245, poa_irradiance__373, poa_irradiance__1083 ¦ Module temperature: module6ne_temp__641 (used), module10nw_temp__640, module1sw_temp__659, module3_temp__639, module5se_temp__660, module6ne_temp__641, module8_temp_bot__637, module8_temp_mid__636, module8_temp_top__635, module_temp_1__253, module_temp_2__254, module_temp_3__255, module_temp_4__257, module_temp_5__258, module_temp_6__259, module_temp_7__260, module_temp_1__381, module_temp_2__382, module_temp_3__383, module_temp_1__1091, module_temp_2__1092, module_temp_3__1093 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__628 ¦ DC Voltage=dc_voltage__630 ¦ DC Current=dc_current__631 ¦ Irradiance=poa_irradiance_2__658 ¦ Module temperature=module6ne_temp__641
my_10_csv_1221.csv | 3.693 | 205.8 | 98.7% retained (1403/1421 rows) | -0.1166 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: ppv_avg__3297 (used), ppv_avg__3297 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3297
my_110_csv_4.csv | 15.422 | 175.6 | 15.7% retained (558/3559 rows) | -0.5613 | yes |  | none | DC Power: dc_power__314 (used), dc_power__314, dc_power__3971, power_factor__327, power_factor__3983, power_factor__3653 ¦ DC Voltage: dc_pos_voltage__316 (used), dc_pos_voltage__316, dc_voltage__3972, inv1_string1_dc_voltage__3627 ¦ DC Current: dc_pos_current__317 (used), dc_pos_current__317, dc_current__3973, inv1_string1_dc_current__3614 ¦ Irradiance: poa_irradiance__313 (used), poa_irradiance__313, poa_irradiance__3970, poa_irradiance__3604, intsolirrad__16, licor1_irradiance__3605, licor2_irradiance__3606, licor3_irradiance__3607, licor4_irradiance__3608, licor5_irradiance__3609, referencemodule1_irradiance__3610, referencemodule2_irradiance__3612 ¦ Module temperature: module_temp_1__321 (used), module_temp_1__321, mod_temperature__3974, module_temp_1__3658 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__314 ¦ DC Voltage=dc_pos_voltage__316 ¦ DC Current=dc_pos_current__317 ¦ Irradiance=poa_irradiance__313 ¦ Module temperature=module_temp_1__321
my_111_csv_4901.csv | 3.603 | 5401.4 | 10.2% retained (367/3593 rows) | -0.7266 | yes |  | none | DC Power: shuntpdc_kw_avg_2__82554 (used), dc_power_inv_14537, shuntpdc_kw_avg_1__82553, shuntpdc_kw_avg_2__82554 ¦ DC Voltage: dc_voltage_other_inv_14537_2 (used), dc_voltage_other_inv_14537, dc_voltage_other_inv_14537_2 ¦ DC Current: shuntcurrent_a_avg_2__82547 (used), shuntcurrent_a_avg_1__82546, shuntcurrent_a_avg_2__82547, shuntcurrent_a_avg_3__82548 ¦ Irradiance: irradiance_poa_o_2198 (used), irradiance_poa_o_2195, irradiance_poa_o_2197, irradiance_poa_o_2198, irradiance_ghi_o_2196, irradiance_poa_o_2199, sewspoairrad_wm2_avg__82524 ¦ Module temperature: temperature_module_o_2201 (used), temperature_module_o_2201 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=shuntpdc_kw_avg_2__82554 ¦ DC Voltage=dc_voltage_other_inv_14537_2 ¦ DC Current=shuntcurrent_a_avg_2__82547 ¦ Irradiance=irradiance_poa_o_2198 ¦ Module temperature=temperature_module_o_2201
my_112_csv_4902.csv | 3.603 | 5973.3 | 13.9% retained (501/3593 rows) | -0.5921 | yes |  | none | DC Power: shuntpdc_kw_avg_1__82651 (used), dc_power_inv_14538, shuntpdc_kw_avg_1__82651, shuntpdc_kw_avg_2__82652 ¦ DC Voltage: dc_voltage_other_inv_14538 (used), dc_voltage_other_inv_14538, dc_voltage_other_inv_14538_2 ¦ DC Current: shuntcurrent_a_avg_3__82646 (used), shuntcurrent_a_avg_1__82644, shuntcurrent_a_avg_2__82645, shuntcurrent_a_avg_3__82646 ¦ Irradiance: irradiance_poa_o_2204 (used), irradiance_ghi_o_2202, irradiance_poa_o_2203, irradiance_poa_o_2204, irradiance_poa_o_2206 ¦ Module temperature: temperature_module_o_2206 (used), temperature_module_o_2206 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=shuntpdc_kw_avg_1__82651 ¦ DC Voltage=dc_voltage_other_inv_14538 ¦ DC Current=shuntcurrent_a_avg_3__82646 ¦ Irradiance=irradiance_poa_o_2204 ¦ Module temperature=temperature_module_o_2206
my_113_csv_4903.csv | 3.603 | 2550.1 | 12.5% retained (450/3592 rows) | -1.0365 | yes |  | none | DC Power: shuntpdc_kw_avg_1__82769 (used), dc_power_inv_14539, shuntpdc_kw_avg_1__82769, shuntpdc_kw_avg_2__82770 ¦ DC Voltage: dc_voltage_other_inv_14539 (used), dc_voltage_other_inv_14539 ¦ DC Current: ac_current_other_inv_14539 (used), ac_current_other_inv_14539, ac_current_other_inv_14539_2, ac_current_other_inv_14539_3 ¦ Irradiance: irradiance_poa_o_2214 (used), irradiance_ghi_o_2206, irradiance_ghi_o_2207, irradiance_ghi_o_2209, irradiance_ghi_o_2210, irradiance_ghi_o_2211, irradiance_ghi_o_2212, irradiance_ghi_o_2213, irradiance_ghi_o_2215, irradiance_ghi_o_2216, irradiance_poa_o_2208, irradiance_poa_o_2214 ¦ Module temperature: temperature_module_o_2218 (used), temperature_module_o_2218 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=shuntpdc_kw_avg_1__82769 ¦ DC Voltage=dc_voltage_other_inv_14539 ¦ DC Current=ac_current_other_inv_14539 ¦ Irradiance=irradiance_poa_o_2214 ¦ Module temperature=temperature_module_o_2218
my_114_csv_50.csv | 200.846 | 503.8 | 10.9% retained (387/3549 rows) | -5.3888 | no | the computed rate (-5.4%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr); the year-over-year changes disagree with each other by about ±12.8%/yr — too scattered for this single number to be trusted | none | DC Power: dc_power_1__765 (used), dc_power__751, dc_power__1136, dc_power__1132, dc_power_1__765, dc_power_2__766, inv1_dc_power__1134, inv2_dc_power__1135, inv1_dc_power__1130, inv2_dc_power__1131, dc_power__628, dc_power__246 ¦ DC Voltage: dc_pos_voltage__753 (used), dc_pos_voltage__753, dc_neg_voltage__755, inv1_dc_voltage__1044 ¦ DC Current: dc_pos_current__754 (used), dc_pos_current__754, dc_neg_current__756, inv1_dc_current__1045 ¦ Irradiance: poa_irradiance__750 (used), poa_irradiance__750, poa_irradiance__1055, poa_irradiance__245, poa_irradiance_refcell__1054, poa_irradiance_1__627, poa_irradiance_2__658 ¦ Module temperature: module_temp_1__760 (used), module_temp_1__760, module_temp__1056, module_temp_1__253 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power_1__765 ¦ DC Voltage=dc_pos_voltage__753 ¦ DC Current=dc_pos_current__754 ¦ Irradiance=poa_irradiance__750 ¦ Module temperature=module_temp_1__760
my_115_csv_51.csv | 28.657 | 1162.8 | 17.3% retained (613/3537 rows) | -1.8001 | no | the year-over-year changes disagree with each other by about ±3.0%/yr — too scattered for this single number to be trusted | none | DC Power: dc_power__772 (used), dc_power__772, dc_power_1__786, dc_power_2__787, dc_power__246, dc_power__406 ¦ DC Voltage: dc_pos_voltage__774 (used), dc_pos_voltage__774, dc_neg_voltage__776, dc_pos_voltage__248 ¦ DC Current: dc_pos_current__775 (used), dc_pos_current__775, dc_neg_current__777, dc_pos_current__249 ¦ Irradiance: poa_irradiance__771 (used), poa_irradiance__771, poa_irradiance__245, poa_irradiance__405 ¦ Module temperature: module_temp_1__781 (used), module_temp_1__781, module_temp_2__782, module_temp_3__783 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__772 ¦ DC Voltage=dc_pos_voltage__774 ¦ DC Current=dc_pos_current__775 ¦ Irradiance=poa_irradiance__771 ¦ Module temperature=module_temp_1__781
my_116_csv_35.csv | 9.782 | 4023.3 | 4.0% retained (142/3584 rows) | -0.9686 | yes |  | none | DC Power: dc_power_hw__2712 (used), dc_power_hw__2712, power_factor_1000__2711 ¦ DC Voltage: dc_voltage__2700 (used), dc_voltage__2700 ¦ DC Current: dc_current__2701 (used), dc_current__2701 ¦ Irradiance: poa_irradiance__2699 (used), poa_irradiance__2699 ¦ Module temperature: module_temp_f__2707 (used), module_temp_f__2707 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power_hw__2712 ¦ DC Voltage=dc_voltage__2700 ¦ DC Current=dc_current__2701 ¦ Irradiance=poa_irradiance__2699 ¦ Module temperature=module_temp_f__2707
my_117_csv_34.csv | 9.859 | 5547.3 | 3.8% retained (137/3589 rows) | -0.2829 | yes |  | none | DC Power: dc_power_hw__2694 (used), dc_power_hw__2694, power_factor_1000__2693 ¦ DC Voltage: dc_voltage__2682 (used), dc_voltage__2682 ¦ DC Current: dc_current__2683 (used), dc_current__2683 ¦ Irradiance: poa_irradiance__2679 (used), poa_irradiance__2679 ¦ Module temperature: module_temp_f__2689 (used), module_temp_f__2689 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power_hw__2694 ¦ DC Voltage=dc_voltage__2682 ¦ DC Current=dc_current__2683 ¦ Irradiance=poa_irradiance__2679 ¦ Module temperature=module_temp_f__2689
my_118_csv_1416.csv | 0.86 | 41953.9 |  |  |  |  | Irradiance | DC Power: dc_power__4742 (used), dc_power__4742, dc_power_positive__4738, dc_power_negative__4741, apparent_power_kva__4745, power_factor__4746, power_factor_pha__4753, power_factor_phb__4754, power_factor_phc__4755, reactive_power_kvar__4744, real_power_kw__4743, real_power_pha_kw__4750, real_power_phb_kw__4751, real_power_phc_kw__4752 ¦ DC Voltage: dc_voltage_positive__4736 (used), dc_voltage_positive__4736, dc_voltage_negative__4739 ¦ DC Current: dc_current_positive__4737 (used), dc_current_positive__4737, dc_current_negative__4740 ¦ Module temperature: enclosure_temp__4735 (used), enclosure_temp__4735, das_temp__4734 |  | Time=measured_on ¦ DC Power=dc_power__4742 ¦ DC Voltage=dc_voltage_positive__4736 ¦ DC Current=dc_current_positive__4737 ¦ Module temperature=enclosure_temp__4735 | No filtering result and degradation rate (stopped at 'duration'): Only ~10 months (<1 year). Degradation correctly not attempted.
my_119_csv_1369.csv | 7.14 | 42845 | 8.9% retained (321/3595 rows) | -0.4715 | yes |  | Irradiance | DC Power: dc_power__3126 (used), dc_power__3126, inv1_dc_power__3167, inv2_dc_power__3168, inv3_dc_power__3169, inv4_dc_power__3170, inv5_dc_power__3171, inv6_dc_power__3172, inv7_dc_power__3173, inv8_dc_power__3174, inv9_dc_power__3175 ¦ DC Voltage: inv1_dc_voltage__3130 (used), inv1_dc_voltage__3130, inv2_dc_voltage__3135, inv3_dc_voltage__3139 ¦ DC Current: inv1_dc_current__3131 (used), inv1_dc_current__3131, inv2_dc_current__3136, inv3_dc_current__3140 ¦ Module temperature: inv1_temp__3129 (used), inv1_temp__3129 | YOY | Time=measured_on ¦ DC Power=dc_power__3126 ¦ DC Voltage=inv1_dc_voltage__3130 ¦ DC Current=inv1_dc_current__3131 ¦ Module temperature=inv1_temp__3129
my_11_csv_1223.csv | 3.693 | 111.1 | 92.6% retained (1316/1421 rows) | -0.1086 | yes |  | Irradiance, Module temperature | DC Power: channel_p (used), channel_p ¦ DC Current: idc1 (used), idc1 | YOY | Time=measured_on ¦ DC Power=channel_p ¦ DC Voltage=computed_dc_voltage ¦ DC Current=idc1
my_120_csv_2045.csv | 1.593 | [5 empty] | DC Power, DC Current | DC Voltage: dc_voltage_o_915 (used), dc_voltage_o_915 ¦ Irradiance: irradiance_ghi_o_913 (used), irradiance_ghi_o_913, irradiance_albedo_o_914, irradiance_albedo_o_916, irradiance_albedo_o_918, irradiance_ghi_o_915, irradiance_ghi_o_917 ¦ Module temperature: temperature_other_o_915 (used), temperature_other_o_915 |  | Time=measured_on ¦ DC Voltage=dc_voltage_o_915 ¦ Irradiance=irradiance_ghi_o_913 ¦ Module temperature=temperature_other_o_915 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_121_csv_1433.csv | 6.992 | 15.4 | 15.8% retained (568/3600 rows) | -1.0953 | yes |  | none | DC Power: kwh_net__5066 (used), kwh_gross__5065, kwh_net__5066 ¦ DC Voltage: dc_voltage__5070 (used), dc_voltage__5070 ¦ Irradiance: poa_irradiance__5061 (used), poa_irradiance__5061 ¦ Module temperature: module_temp__5063 (used), module_temp__5063 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=kwh_net__5066 ¦ DC Voltage=dc_voltage__5070 ¦ DC Current=computed_dc_current ¦ Irradiance=poa_irradiance__5061 ¦ Module temperature=module_temp__5063
my_122_csv_1431.csv | 8.041 | 339313.6 | 3.5% retained (125/3585 rows) | -2.4866 | no | only 15 daily data point(s) survived filtering (a reliable trend needs at least 20) | none | DC Power: dc_power__5089 (used), dc_power__5089 ¦ DC Voltage: dc_voltage__5087 (used), dc_voltage__5087 ¦ DC Current: dc_current__5088 (used), dc_current__5088 ¦ Irradiance: poa_irradiance__5078 (used), poa_irradiance__5078 ¦ Module temperature: module_temp__5080 (used), module_temp__5080 | YOY | Time=measured_on ¦ DC Power=dc_power__5089 ¦ DC Voltage=dc_voltage__5087 ¦ DC Current=dc_current__5088 ¦ Irradiance=poa_irradiance__5078 ¦ Module temperature=module_temp__5080
my_123_csv_1418.csv | 3.584 | 3024334.8 | 9.3% retained (225/2421 rows) | 3.7977 | no | the computed rate (+3.8%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current | DC Power: ac_power_1_kwac__4786 (used), ac_power__5048, ac_power_1_kwac__4786, ac_power_2_kwac__4788, ac_power_3_kwac__4790 ¦ Irradiance: poa_irradiance_sun__4785 (used), poa_irradiance_sun__4785 ¦ Module temperature: module_temp_f_temp2__4793 (used), module_temp_f_temp2__4793 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=ac_power_1_kwac__4786 ¦ Irradiance=poa_irradiance_sun__4785 ¦ Module temperature=module_temp_f_temp2__4793
my_12_csv_1225.csv | 3.693 | 209.2 | 98.7% retained (1401/1420 rows) | -0.0953 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: meas_pwr (used), meas_pwr | YOY | Time=measured_on ¦ DC Power=meas_pwr
my_13_csv_1229.csv | 6.533 | 494 | 1.9% retained (28/1440 rows) | -7.71 | no | the computed rate (-7.7%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr); the year-over-year changes disagree with each other by about ±7.2%/yr — too scattered for this single number to be trusted | none | DC Power: dc_power__886 (used), dc_power__886 ¦ DC Voltage: dc_voltage__885 (used), dc_voltage__885 ¦ Irradiance: gh_irradiance__880 (used), gh_irradiance__880 ¦ Module temperature: module_temp_south_f__881 (used), module_temp_south_f__881 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__886 ¦ DC Voltage=dc_voltage__885 ¦ DC Current=computed_dc_current ¦ Irradiance=gh_irradiance__880 ¦ Module temperature=module_temp_south_f__881
my_14_csv_1230.csv | 4.914 | 493.7 | 35.0% retained (469/1340 rows) | -3.0006 | no | the computed rate (-3.0%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: dc_power__889 (used), dc_power__889 | YOY | Time=measured_on ¦ DC Power=dc_power__889
my_15_csv_1244.csv | 3.326 | 252.5 | 98.5% retained (1405/1426 rows) | -0.1552 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3346 (used), ppv_avg__3346 ¦ DC Current: a_avg__3347 (used), a_avg__3347 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3346 ¦ DC Current=a_avg__3347
my_16_csv_1246.csv | 3.499 | 240.7 | 96.5% retained (1369/1418 rows) | -0.0062 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: ppv_avg__3354 (used), ppv_avg__3354 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3354
my_17_csv_1248.csv | 3.493 | [5 empty] | DC Power, DC Voltage, Irradiance, Module temperature | DC Current: idc1 (used), idc1 |  | Time=measured_on ¦ DC Current=idc1 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_18_csv_1249.csv | 2.097 | 249.8 | 98.1% retained (1397/1424 rows) | -0.036 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: channel_p (used), channel_p | YOY | Time=measured_on ¦ DC Power=channel_p
my_19_csv_1250.csv | 4.589 | 123.5 | 93.5% retained (1338/1431 rows) | -0.0252 | yes |  | Irradiance, Module temperature | DC Power: ppv_avg__3370 (used), ppv_avg__3370 ¦ DC Current: a_avg__3371 (used), a_avg__3371 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3370 ¦ DC Voltage=computed_dc_voltage ¦ DC Current=a_avg__3371
my_20_csv_1252.csv | 3.472 | 244.7 | 98.7% retained (1407/1425 rows) | 0.0613 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3378 (used), ppv_avg__3378 ¦ DC Current: a_avg__3379 (used), a_avg__3379 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3378 ¦ DC Current=a_avg__3379
my_21_csv_1253.csv | 3.655 | 120.9 | 97.7% retained (1385/1418 rows) | -0.09 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: ppv_avg__3382 (used), ppv_avg__3382 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3382
my_22_csv_1254.csv | 2.281 | 249.7 | 99.4% retained (1412/1421 rows) | -0.8213 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: ppv_avg__3386 (used), ppv_avg__3386 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3386
my_23_csv_1255.csv | 3.496 | 250 | 99.8% retained (1427/1430 rows) | -0.06 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: p_out (used), p_out ¦ DC Current: idc1 (used), idc1 | YOY | Time=measured_on ¦ DC Power=p_out ¦ DC Current=idc1
my_24_csv_1256.csv | 2.606 | 247514 | 95.8% retained (1375/1435 rows) | 0.3582 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: output_kw (used), output_kw | YOY | Time=measured_on ¦ DC Power=output_kw
my_25_csv_1257.csv | 3.493 | 249.2 | 95.9% retained (1369/1427 rows) | -0.598 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3398 (used), ppv_avg__3398 ¦ DC Current: a_avg__3399 (used), a_avg__3399 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3398 ¦ DC Current=a_avg__3399
my_26_csv_1258.csv | 3.524 | 249.5 | 95.2% retained (1355/1424 rows) | -0.9951 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3402 (used), ppv_avg__3402 ¦ DC Current: a_avg__3403 (used), a_avg__3403 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3402 ¦ DC Current=a_avg__3403
my_27_csv_1261.csv | 2.355 | 249.7 | 94.2% retained (1344/1427 rows) | 0.1911 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3414 (used), ppv_avg__3414 ¦ DC Current: a_avg__3415 (used), a_avg__3415 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3414 ¦ DC Current=a_avg__3415
my_28_csv_1263.csv | 3.562 | 251.4 | 99.1% retained (1404/1417 rows) | -0.0273 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: ppv_avg__3422 (used), ppv_avg__3422 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3422
my_29_csv_1264.csv | 3.721 | 249.2 | 93.2% retained (1321/1417 rows) | 0.1821 | yes |  | Irradiance, Module temperature | DC Power: pwr (used), pwr ¦ DC Current: idc1 (used), idc1 | YOY | Time=measured_on ¦ DC Power=pwr ¦ DC Voltage=computed_dc_voltage ¦ DC Current=idc1
my_30_csv_1265.csv | 3.504 | 251.6 | 99.4% retained (1427/1436 rows) | -0.1919 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: p_out (used), p_out | YOY | Time=measured_on ¦ DC Power=p_out
my_31_csv_1266.csv | 3.499 | 234.8 | 96.0% retained (1360/1417 rows) | 0.0035 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3434 (used), ppv_avg__3434 ¦ DC Current: a_avg__3435 (used), a_avg__3435 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3434 ¦ DC Current=a_avg__3435
my_32_csv_1268.csv | 3.718 | 252.2 | 96.7% retained (1349/1395 rows) | 0.0677 | yes |  | Irradiance, Module temperature | DC Power: ppv_avg__3442 (used), ppv_avg__3442 ¦ DC Current: a_avg__3443 (used), a_avg__3443 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3442 ¦ DC Voltage=computed_dc_voltage ¦ DC Current=a_avg__3443
my_33_csv_1269.csv | 3.502 | 252.8 | 97.3% retained (1392/1430 rows) | 0.1676 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3446 (used), ppv_avg__3446 ¦ DC Current: a_avg__3447 (used), a_avg__3447 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3446 ¦ DC Current=a_avg__3447
my_34_csv_1270.csv | 3.592 | 250.3 | 96.3% retained (1365/1417 rows) | -0.0663 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: ppv_avg__3450 (used), ppv_avg__3450 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3450
my_35_csv_1271.csv | 3.474 | 251.4 | 97.4% retained (1390/1427 rows) | -0.0223 | yes |  | Irradiance, Module temperature | DC Power: p_dc_meas (used), p_dc_meas ¦ DC Current: idc1 (used), idc1 | YOY | Time=measured_on ¦ DC Power=p_dc_meas ¦ DC Voltage=computed_dc_voltage ¦ DC Current=idc1
my_36_csv_1272.csv | 3.666 | 248.2 | 97.7% retained (1384/1417 rows) | -0.2644 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: pwr (used), pwr | YOY | Time=measured_on ¦ DC Power=pwr
my_37_csv_1273.csv | 3.71 | 125.5 | 99.2% retained (1400/1411 rows) | -0.0296 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3462 (used), ppv_avg__3462 ¦ DC Current: a_avg__3463 (used), a_avg__3463 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3462 ¦ DC Current=a_avg__3463
my_38_csv_1274.csv | 2.333 | 250.2 | 98.0% retained (1391/1420 rows) | -1.6739 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: ppv_avg__3466 (used), ppv_avg__3466 ¦ DC Current: a_avg__3467 (used), a_avg__3467 | YOY | Time=measured_on ¦ DC Power=ppv_avg__3466 ¦ DC Current=a_avg__3467
my_39_csv_1276.csv | 8.775 | 2799.2 | 4.4% retained (63/1417 rows) | -0.1592 | no | only 8 daily data point(s) survived filtering (a reliable trend needs at least 20) | DC Voltage, DC Current, Module temperature | DC Power: dc_power_hw__3039 (used), dc_power_hw__3039 ¦ Irradiance: poa_irradiance__3026 (used), poa_irradiance__3026 | LR | Time=measured_on ¦ DC Power=dc_power_hw__3039 ¦ Irradiance=poa_irradiance__3026
my_40_csv_1277.csv | 2.648 | 5298.8 | 23.1% retained (332/1440 rows) | -3.8588 | no | the computed rate (-3.9%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: dc_power_hw__3054 (used), dc_power_hw__3054 | YOY | Time=measured_on ¦ DC Power=dc_power_hw__3054
my_41_csv_1278.csv | 8.758 | 32588.8 | 8.1% retained (115/1417 rows) | -5.3427 | no | only 17 daily data point(s) survived filtering (a reliable trend needs at least 20); the computed rate (-5.3%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current | DC Power: val_power (used), val_power ¦ Irradiance: g1 (used), g1 ¦ Module temperature: tm1 (used), tm1 | YOY | Time=measured_on ¦ DC Power=val_power ¦ Irradiance=g1 ¦ Module temperature=tm1
my_42_csv_1283.csv | 8.427 | 67899.4 | 12.0% retained (161/1344 rows) | 1.81 | no | the computed rate (+1.8%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr); the year-over-year changes disagree with each other by about ±4.7%/yr — too scattered for this single number to be trusted | DC Voltage, DC Current, Module temperature | DC Power: p_dc_meas (used), p_dc_meas ¦ Irradiance: plane_irr (used), plane_irr | YOY (energy-ratio) | Time=measured_on ¦ DC Power=p_dc_meas ¦ Irradiance=plane_irr
my_43_csv_1284.csv | 2.667 | 247.4 | 12.9% retained (184/1430 rows) | 0.7756 | no | the computed rate (+0.8%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | none | DC Power: dc_power__943 (used), dc_power__943 ¦ DC Voltage: dc_pos_voltage__945 (used), dc_pos_voltage__945 ¦ DC Current: dc_pos_current__946 (used), dc_pos_current__946 ¦ Irradiance: poa_irradiance_2__942 (used), poa_irradiance_2__942 ¦ Module temperature: module_temp_1__950 (used), module_temp_1__950 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=dc_power__943 ¦ DC Voltage=dc_pos_voltage__945 ¦ DC Current=dc_pos_current__946 ¦ Irradiance=poa_irradiance_2__942 ¦ Module temperature=module_temp_1__950
my_44_csv_1289.csv | 7.529 | 325.1 | 31.7% retained (441/1389 rows) | -7.2028 | no | the computed rate (-7.2%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance | DC Power: dc_power__1059 (used), dc_power__1059 ¦ DC Voltage: dc_pos_voltage__1061 (used), dc_pos_voltage__1061 ¦ DC Current: dc_pos_current__1062 (used), dc_pos_current__1062 ¦ Module temperature: module_temp_1__1066 (used), module_temp_1__1066 | YOY | Time=measured_on ¦ DC Power=dc_power__1059 ¦ DC Voltage=dc_pos_voltage__1061 ¦ DC Current=dc_pos_current__1062 ¦ Module temperature=module_temp_1__1066
my_45_csv_1300.csv | 5.405 | 466.8 | 9.5% retained (124/1312 rows) | -0.477 | no | only 16 daily data point(s) survived filtering (a reliable trend needs at least 20) | Module temperature | DC Power: dc_power_calc__36 (used), dc_power_calc__36 ¦ DC Voltage: dc_voltage__35 (used), dc_voltage__35 ¦ DC Current: dc_current__32 (used), dc_current__32 ¦ Irradiance: intsolirrad__26 (used), intsolirrad__26 | YOY | Time=measured_on ¦ DC Power=dc_power_calc__36 ¦ DC Voltage=dc_voltage__35 ¦ DC Current=dc_current__32 ¦ Irradiance=intsolirrad__26
my_46_csv_1305.csv | 2.576 | 832.1 | 41.4% retained (533/1287 rows) | 0.0285 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: dc_power_1_calc__63 (used), dc_power_1_calc__63 | YOY | Time=measured_on ¦ DC Power=dc_power_1_calc__63
my_47_csv_1307.csv | 3.934 | 849.6 | 1.8% retained (23/1279 rows) | 14.4328 | no | only 4 daily data point(s) survived filtering (a reliable trend needs at least 20); the computed rate (+14.4%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | none | DC Power: meas_pwr (used), meas_pwr ¦ DC Voltage: vdc1 (used), vdc1 ¦ DC Current: idc1 (used), idc1 ¦ Irradiance: g1 (used), g1 ¦ Module temperature: tm1 (used), tm1 | YOY | Time=measured_on ¦ DC Power=meas_pwr ¦ DC Voltage=vdc1 ¦ DC Current=idc1 ¦ Irradiance=g1 ¦ Module temperature=tm1
my_48_csv_1308.csv | 4.145 | 2860.2 | 5.6% retained (67/1188 rows) | 35.0302 | no | the computed rate (+35.0%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr); the year-over-year changes disagree with each other by about ±14.6%/yr — too scattered for this single number to be trusted | DC Voltage, DC Current, Module temperature | DC Power: val_power (used), val_power ¦ Irradiance: plane_irr (used), plane_irr | YOY (energy-ratio) | Time=measured_on ¦ DC Power=val_power ¦ Irradiance=plane_irr
my_49_csv_1310.csv | 5.251 | 10229.3 | 2.6% retained (37/1408 rows) | 10.3547 | no | only 9 daily data point(s) survived filtering (a reliable trend needs at least 20); the computed rate (+10.4%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | none | DC Power: dc_power_1_6__172 (used), dc_power_1_6__172 ¦ DC Voltage: dc_voltage_1__142 (used), dc_voltage_1__142 ¦ DC Current: dc_current_1__141 (used), dc_current_1__141 ¦ Irradiance: intsolirrad__136 (used), intsolirrad__136 ¦ Module temperature: module_temp_f__138 (used), module_temp_f__138 | LR | Time=measured_on ¦ DC Power=dc_power_1_6__172 ¦ DC Voltage=dc_voltage_1__142 ¦ DC Current=dc_current_1__141 ¦ Irradiance=intsolirrad__136 ¦ Module temperature=module_temp_f__138
my_50_csv_1332.csv | 8.652 | 189499.7 | 12.8% retained (183/1428 rows) | -4.6631 | no | the computed rate (-4.7%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance, Module temperature | DC Power: dc_power__2655 (used), dc_power__2655 ¦ DC Voltage: inv1_dc_voltage__2644 (used), inv1_dc_voltage__2644 ¦ DC Current: inv1_dc_current__2645 (used), inv1_dc_current__2645 | YOY | Time=measured_on ¦ DC Power=dc_power__2655 ¦ DC Voltage=inv1_dc_voltage__2644 ¦ DC Current=inv1_dc_current__2645
my_51_csv_1200.csv | 5.823 | -0.1 | 20.9% retained (754/3600 rows) | -3.6611 | no | the computed rate (-3.7%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: power_factor__4198 (used), power_factor__4198 | YOY | Time=measured_on ¦ DC Power=power_factor__4198
my_52_csv_1202.csv | 9.415 | -0.1 | 0.6% retained (22/3586 rows) | -0.5303 | no | only 6 daily data point(s) survived filtering (a reliable trend needs at least 20) | Irradiance | DC Power: power_factor__2805 (used), dc_power__2841, inv1_dc_power__2811, inv2_dc_power__2816, inv3_dc_power__2821, inv4_dc_power__2826, inv5_dc_power__2831, inv6_dc_power__2836, power_factor__2805 ¦ DC Voltage: inv1_dc_voltage__2812 (used), inv1_dc_voltage__2812, inv2_dc_voltage__2817, inv3_dc_voltage__2822 ¦ DC Current: inv1_dc_current__2813 (used), inv1_dc_current__2813, inv2_dc_current__2818, inv3_dc_current__2823 ¦ Irradiance: poa_irradiance__2806 ¦ Module temperature: module_temp_k__2808 (used), module_temp_k__2808 | LR | Time=measured_on ¦ DC Power=power_factor__2805 ¦ DC Voltage=inv1_dc_voltage__2812 ¦ DC Current=inv1_dc_current__2813 ¦ Module temperature=module_temp_k__2808
my_53_csv_1207.csv | 0.873 | 3172.2 |  |  |  |  | none | DC Power: dc_power__2622 (used), dc_power__2622, dc_power_a1__2623, dc_power_a2__2624, dc_power_b1__2625, dc_power_b2__2626, dc_power_c1__2627, dc_power_c2__2628 ¦ DC Voltage: dc_voltage_a__2635 (used), dc_voltage_a__2635, dc_voltage_b__2636, dc_voltage_c__2637 ¦ Irradiance: poa_irradiance_lp02_2__2634 (used), poa_irradiance__2633, poa_irradiance_cs300_1__2630, poa_irradiance_cs300_2__2631, poa_irradiance_lp02_2__2634 ¦ Module temperature: module_temp__2629 (used), module_temp__2629 |  | Time=measured_on ¦ DC Power=dc_power__2622 ¦ DC Voltage=dc_voltage_a__2635 ¦ DC Current=computed_dc_current ¦ Irradiance=poa_irradiance_lp02_2__2634 ¦ Module temperature=module_temp__2629 | No filtering result and degradation rate (stopped at 'duration'): Only ~10 months (<1 year). Degradation correctly not attempted.
my_54_csv_1216.csv | 3.732 | 93.7 | 30.7% retained (1099/3581 rows) | 0.4122 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: wh_n_sum__3189 (used), wh_n_sum__3189 ¦ Irradiance: a_avg__3192 | YOY | Time=measured_on ¦ DC Power=wh_n_sum__3189
my_55_csv_1218.csv | 3.732 | 86.5 | 32.9% retained (1155/3512 rows) | 0.3419 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: wh_n_sum__3271 (used), wh_n_sum__3271 | YOY | Time=measured_on ¦ DC Power=wh_n_sum__3271
my_56_csv_1220.csv | 3.732 | [5 empty] | DC Power, DC Voltage, DC Current, Irradiance, Module temperature | none |  | Time=measured_on | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_57_csv_1222.csv | 3.732 | 92.6 | 31.3% retained (1100/3512 rows) | 0.2117 | yes |  | DC Voltage, Irradiance, Module temperature | DC Power: wh_n_sum__3304 (used), wh_n_sum__3304 ¦ DC Current: w_n_avg__3305 (used), w_n_avg__3305 | YOY | Time=measured_on ¦ DC Power=wh_n_sum__3304 ¦ DC Current=w_n_avg__3305
my_58_csv_1224.csv | 3.732 | 78.4 | 27.6% retained (968/3512 rows) | -7.8561 | no | the computed rate (-7.9%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: wh_n_sum__3319 (used), wh_n_sum__3319 | YOY | Time=measured_on ¦ DC Power=wh_n_sum__3319
my_59_csv_1226.csv | 3.732 | 43.5 | 32.1% retained (1128/3511 rows) | -1.3605 | yes |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: wh_n_sum__3335 (used), wh_n_sum__3335 | YOY | Time=measured_on ¦ DC Power=wh_n_sum__3335
my_60_csv_1228.csv | 2.757 | [5 empty] | DC Power, DC Voltage, DC Current, Irradiance | Module temperature: module_temp_10__1036 (used), module_temp_10__1036, module_temp_11__1037, module_temp_12__1038 |  | Time=measured_on ¦ Module temperature=module_temp_10__1036 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_61_csv_1231.csv | 5.459 | 444.6 | 15.5% retained (554/3570 rows) | -2.5663 | no | the year-over-year changes disagree with each other by about ±2.2%/yr — too scattered for this single number to be trusted | DC Voltage, DC Current | DC Power: ac_power__896 (used), ac_power__896 ¦ Irradiance: poa_irradiance__893 (used), poa_irradiance__893, gh_irradiance__894 ¦ Module temperature: ambient_temp_f__895 (used), ambient_temp_f__895 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=ac_power__896 ¦ Irradiance=poa_irradiance__893 ¦ Module temperature=ambient_temp_f__895
my_62_csv_1239.csv | 8.797 | 318388.4 | 1.4% retained (51/3577 rows) | 1.0325 | no | the computed rate (+1.0%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr); the year-over-year changes disagree with each other by about ±2.9%/yr — too scattered for this single number to be trusted | DC Voltage, DC Current | DC Power: ac_power_metered_kw__3015 (used), ac_power_metered_kw__3015 ¦ Irradiance: poa_irradiance__3018 (used), poa_irradiance__3018 ¦ Module temperature: module_temp_f__3019 (used), module_temp_f__3019 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=ac_power_metered_kw__3015 ¦ Irradiance=poa_irradiance__3018 ¦ Module temperature=module_temp_f__3019
my_63_csv_1245.csv | 0.394 | 250.7 |  |  |  |  | Irradiance, Module temperature | DC Power: ppv_avg__3350 (used), ppv_avg__3350 ¦ DC Current: a_avg__3351 (used), a_avg__3351 |  | Time=measured_on ¦ DC Power=ppv_avg__3350 ¦ DC Voltage=computed_dc_voltage ¦ DC Current=a_avg__3351 | No filtering result and degradation rate (stopped at 'duration'): Only ~5 months (<1 year). Degradation correctly not attempted.
my_64_csv_1259.csv | 1.782 | 246.2 | 2.9% retained (105/3600 rows) | 0.5413 | no | the data spans only 1.8 year(s) — under 2 years is too short to separate real aging from seasonal weather; the computed rate (+0.5%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Module temperature | DC Power: ppv_avg__3406 (used), ppv_avg__3406 ¦ Irradiance: wh_sum__3404 (used), wh_sum__3404 | LR | Time=measured_on ¦ DC Power=ppv_avg__3406 ¦ Irradiance=wh_sum__3404
my_65_csv_1260.csv | 0.687 | 244.1 |  |  |  |  | Module temperature | DC Power: ppv_avg__3410 (used), ppv_avg__3410 ¦ DC Current: a_avg__3411 (used), a_avg__3411 ¦ Irradiance: wh_sum__3408 (used), wh_sum__3408 |  | Time=measured_on ¦ DC Power=ppv_avg__3410 ¦ DC Voltage=computed_dc_voltage ¦ DC Current=a_avg__3411 ¦ Irradiance=wh_sum__3408 | No filtering result and degradation rate (stopped at 'duration'): Only ~8 months (<1 year). Degradation correctly not attempted.
my_66_csv_1262.csv | 1.106 | 250.2 | 9.1% retained (321/3532 rows) | 0.0232 | no | the data spans only 1.1 year(s) — under 2 years is too short to separate real aging from seasonal weather | Module temperature | DC Power: ppv_avg__3418 (used), ppv_avg__3418 ¦ DC Current: a_avg__3419 (used), a_avg__3419 ¦ Irradiance: w_avg__3417 (used), w_avg__3417 | LR | Time=measured_on ¦ DC Power=ppv_avg__3418 ¦ DC Voltage=computed_dc_voltage ¦ DC Current=a_avg__3419 ¦ Irradiance=w_avg__3417
my_67_csv_1267.csv | 0.808 | 253.1 |  |  |  |  | Irradiance, Module temperature | DC Power: ppv_avg__3438 (used), ppv_avg__3438 ¦ DC Current: a_avg__3439 (used), a_avg__3439 |  | Time=measured_on ¦ DC Power=ppv_avg__3438 ¦ DC Voltage=computed_dc_voltage ¦ DC Current=a_avg__3439 | No filtering result and degradation rate (stopped at 'duration'): Only ~10 months (<1 year). Degradation correctly not attempted.
my_68_csv_1275.csv | 3.028 | 3569 | 31.1% retained (1095/3526 rows) | -5.1087 | no | the computed rate (-5.1%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance, Module temperature | DC Power: ac_power_metered_kw__3023 (used), ac_power_metered_kw__3023 ¦ DC Voltage: ac_voltage__3024 (used), ac_voltage__3024 ¦ DC Current: ac_current__3025 (used), ac_current__3025 | YOY | Time=measured_on ¦ DC Power=ac_power_metered_kw__3023 ¦ DC Voltage=ac_voltage__3024 ¦ DC Current=ac_current__3025
my_69_csv_1294.csv | 3.332 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__1 (used), intsolirrad__1 ¦ Module temperature: module_temp_f__3 (used), module_temp_f__3 |  | Time=measured_on ¦ Irradiance=intsolirrad__1 ¦ Module temperature=module_temp_f__3 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_70_csv_1295.csv | 3.441 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__6 (used), intsolirrad__6 ¦ Module temperature: module_temp_f__8 (used), module_temp_f__8 |  | Time=measured_on ¦ Irradiance=intsolirrad__6 ¦ Module temperature=module_temp_f__8 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_71_csv_1296.csv | 1.834 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__11 (used), intsolirrad__11 ¦ Module temperature: module_temp_f__13 (used), module_temp_f__13 |  | Time=measured_on ¦ Irradiance=intsolirrad__11 ¦ Module temperature=module_temp_f__13 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_72_csv_1297.csv | 1.079 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__858 (used), intsolirrad__858 ¦ Module temperature: module_temp_f__860 (used), module_temp_f__860 |  | Time=measured_on ¦ Irradiance=intsolirrad__858 ¦ Module temperature=module_temp_f__860 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_73_csv_1298.csv | 5.432 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__16 (used), intsolirrad__16 ¦ Module temperature: module_temp_f__18 (used), module_temp_f__18 |  | Time=measured_on ¦ Irradiance=intsolirrad__16 ¦ Module temperature=module_temp_f__18 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_74_csv_1299.csv | 4.378 | 690.8 | 0.0% retained (0/3548 rows) |  |  |  | none | DC Power: computed_dc_power (used), dc_power__406 ¦ DC Voltage: dc_pos_voltage__408 (used), dc_pos_voltage__408 ¦ DC Current: dc_pos_current__409 (used), dc_pos_current__409 ¦ Irradiance: intsolirrad__21 (used), poa_irradiance__405, intsolirrad__21 ¦ Module temperature: module_temp_f__23 (used), module_temp_f__23, module_temp_1__413, module_temp_2__414 | YOY | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=dc_pos_voltage__408 ¦ DC Current=dc_pos_current__409 ¦ Irradiance=intsolirrad__21 ¦ Module temperature=module_temp_f__23 | No degradation rate (stopped at 'filter'): Only 0 row(s) survived filtering (need >= 20) -- not enough clean data to estimate degradation. Correctly refused rather than guessing.
my_75_csv_1301.csv | 5.547 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__38 (used), intsolirrad__38 ¦ Module temperature: module_temp_f__40 (used), module_temp_f__40 |  | Time=measured_on ¦ Irradiance=intsolirrad__38 ¦ Module temperature=module_temp_f__40 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_76_csv_1302.csv | 5.503 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__43 (used), intsolirrad__43 ¦ Module temperature: module_temp_f__45 (used), module_temp_f__45 |  | Time=measured_on ¦ Irradiance=intsolirrad__43 ¦ Module temperature=module_temp_f__45 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_77_csv_1303.csv | 3.562 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__48 (used), intsolirrad__48 ¦ Module temperature: module_temp_f__50 (used), module_temp_f__50 |  | Time=measured_on ¦ Irradiance=intsolirrad__48 ¦ Module temperature=module_temp_f__50 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_78_csv_1304.csv | 3.485 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__200 (used), intsolirrad__200 ¦ Module temperature: module_temp_f__202 (used), module_temp_f__202 |  | Time=measured_on ¦ Irradiance=intsolirrad__200 ¦ Module temperature=module_temp_f__202 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_79_csv_1306.csv | 1.109 | 1930.4 | 5.8% retained (206/3565 rows) | 33.3671 | no | the data spans only 1.1 year(s) — under 2 years is too short to separate real aging from seasonal weather; the computed rate (+33.4%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | none | DC Power: dc_power_2_calc__234 (used), dc_power_1_6__240, dc_power_1_calc__233, dc_power_2_calc__234, dc_power_3_calc__235, dc_power_4_calc__236, dc_power_5_calc__237, dc_power_6_calc__238 ¦ DC Voltage: dc_voltage_2__214 (used), dc_voltage_1__210, dc_voltage_2__214, dc_voltage_3__218 ¦ DC Current: dc_current_1__209 (used), dc_current_1__209, dc_current_2__213, dc_current_3__217 ¦ Irradiance: intsolirrad__204 (used), intsolirrad__204 ¦ Module temperature: module_temp_f__206 (used), module_temp_f__206 | LR | Time=measured_on ¦ DC Power=dc_power_2_calc__234 ¦ DC Voltage=dc_voltage_2__214 ¦ DC Current=dc_current_1__209 ¦ Irradiance=intsolirrad__204 ¦ Module temperature=module_temp_f__206
my_80_csv_1309.csv | 3.075 | [5 empty] | DC Power, DC Voltage, DC Current | Irradiance: intsolirrad__131 (used), intsolirrad__131 ¦ Module temperature: module_temp_f__133 (used), module_temp_f__133 |  | Time=measured_on ¦ Irradiance=intsolirrad__131 ¦ Module temperature=module_temp_f__133 | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable DC Power column found, so degradation can't be computed.
my_81_csv_1311.csv | 0.608 | 0 |  |  |  |  | none | DC Power: computed_dc_power (used), dc_power__246, dc_power__4025, dc_power__628, dc_power__422, dc_power__1084, power_factor__1097, dc_power__374, power_factor__387 ¦ DC Voltage: dc_pos_voltage__248 (used), dc_pos_voltage__248, dc_voltage__4023, dc_pos_voltage__424 ¦ DC Current: dc_pos_current__249 (used), dc_pos_current__249, dc_current__4024, dc_current__631 ¦ Irradiance: intsolirrad__241 (used), poa_irradiance__245, poa_irradiance__4022, poa_irradiance__421, intsolirrad__241, poa_irradiance_1__627, poa_irradiance_2__658, gh_irradiance__1217, irradiance_average__1224, irradiance_stability__1225, poa_irradiance__1083, poa_irradiance__373 ¦ Module temperature: module_temp_f__243 (used), module_temp_f__243, module_temp_1__253, module_temp_2__254 |  | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=dc_pos_voltage__248 ¦ DC Current=dc_pos_current__249 ¦ Irradiance=intsolirrad__241 ¦ Module temperature=module_temp_f__243 | No filtering result and degradation rate (stopped at 'duration'): Only ~7 months (<1 year). Degradation correctly not attempted.
my_82_csv_1312.csv | 1.448 | 1543.4 | 2.6% retained (62/2417 rows) | 34.6078 | no | only 10 daily data point(s) survived filtering (a reliable trend needs at least 20); the data spans only 1.4 year(s) — under 2 years is too short to separate real aging from seasonal weather; the computed rate (+34.6%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | none | DC Power: dc_power_2_calc__190 (used), dc_power__198, dc_power_1_calc__184, dc_power_2_calc__190, dc_power_3_calc__196 ¦ DC Voltage: dc_voltage_2__189 (used), dc_voltage_1__183, dc_voltage_2__189, dc_voltage_3__195 ¦ DC Current: dc_current_1__180 (used), dc_current_1__180, dc_current_2__186, dc_current_3__192 ¦ Irradiance: intsolirrad__174 (used), intsolirrad__174 ¦ Module temperature: module_temp_f__176 (used), module_temp_f__176, module_temp_5_1__4821, unbiased_module_temp_3_1__1195 | LR | Time=measured_on ¦ DC Power=dc_power_2_calc__190 ¦ DC Voltage=dc_voltage_2__189 ¦ DC Current=dc_current_1__180 ¦ Irradiance=intsolirrad__174 ¦ Module temperature=module_temp_f__176
my_83_csv_1314.csv | 3.302 | 1599 | 93.9% retained (3319/3536 rows) | 40.8596 | no | the computed rate (+40.9%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance, Module temperature | DC Power: whtotal__263 (used), whtotal__263 ¦ DC Voltage: vatotal__262 (used), vatotal__262 | YOY | Time=measured_on ¦ DC Power=whtotal__263 ¦ DC Voltage=vatotal__262 ¦ DC Current=computed_dc_current
my_84_csv_1315.csv | 1.763 | 235 | 0.0% retained (1/3434 rows) |  |  |  | Irradiance | DC Power: computed_dc_power (used), dc_power__422, dc_power__246, dc_power__374, dc_power__3971, power_factor__3983, dc_power__1084, dc_power__628, power_factor__1097, power_factor__387, dc_power__583, power_factor__596, dc_power__1132, inv1_dc_power__1130, inv2_dc_power__1131 ¦ DC Voltage: dc_pos_voltage__248 (used), dc_pos_voltage__424, dc_pos_voltage__248, dc_voltage__3972 ¦ DC Current: dc_pos_current__249 (used), dc_pos_current__425, dc_pos_current__249, dc_current__3973 ¦ Irradiance: poa_irradiance__421, poa_irradiance__245, poa_irradiance__373, poa_irradiance__3970, poa_irradiance_1__627, poa_irradiance_2__658, poa_irradiance__1083, poa_irradiance__582, clean_poa__11740, dirty_poa__11742 ¦ Module temperature: module_temp_1__253 (used), module_temp_1__429, module_temp_1__253, panel_temperature__11739 | LR | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=dc_pos_voltage__248 ¦ DC Current=dc_pos_current__249 ¦ Module temperature=module_temp_1__253 | No degradation rate (stopped at 'filter'): Only 1 row(s) survived filtering (need >= 20) -- not enough clean data to estimate degradation. Correctly refused rather than guessing.
my_85_csv_1316.csv | 1.175 | 142.3 | 0.0% retained (1/3266 rows) |  |  |  | Irradiance | DC Power: computed_dc_power (used), dc_power__4025, dc_power__1132, dc_power__628, power_factor__3653, dc_power__406, dc_power__374, power_factor__387, dc_power__389, inv1_dc_power__1130, inv2_dc_power__1131, dc_power_1__765, dc_power_2__766, dc_power__751, dc_power__246 ¦ DC Voltage: dc_pos_voltage__376 (used), dc_voltage__4023, dc_pos_voltage__408, dc_pos_voltage__376 ¦ DC Current: dc_pos_current__377 (used), dc_current__4024, dc_pos_current__409, dc_pos_current__377 ¦ Irradiance: poa_irradiance__405, poa_irradiance__4022, poa_irradiance__388, licor1_irradiance__3605, licor2_irradiance__3606, licor3_irradiance__3607, licor4_irradiance__3608, licor5_irradiance__3609, poa_irradiance__3604, referencemodule1_irradiance__3610, referencemodule2_irradiance__3612, intsolirrad__16, poa_irradiance__373, poa_irradiance_1__627, poa_irradiance_2__658, poa_irradiance__750, poa_irradiance__245 ¦ Module temperature: module_temp_1__381 (used), module_temp_1__413, module_temp_1__396, module_temp_1__381 | LR | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=dc_pos_voltage__376 ¦ DC Current=dc_pos_current__377 ¦ Module temperature=module_temp_1__381 | No degradation rate (stopped at 'filter'): Only 1 row(s) survived filtering (need >= 20) -- not enough clean data to estimate degradation. Correctly refused rather than guessing.
my_86_csv_1317.csv | 0 | 1011.5 |  |  |  |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: vatotal__269 (used), vatotal__269, whtotal__270 |  | Time=measured_on ¦ DC Power=vatotal__269 | No filtering result and degradation rate (stopped at 'duration'): Only ~0 months (<1 year). Degradation correctly not attempted.
my_87_csv_1318.csv | 4.279 | 26.1 | 0.0% retained (1/3540 rows) |  |  |  | Irradiance | DC Power: computed_dc_power (used), dc_power__628, dc_power__246, dc_power__374, dc_power_mod1__3848, dc_power_mod2__3849, dc_power_mod3__3850, dc_power_mod4__3851, power_factor_1__3872, power_factor_2__3884, power_factor_3__3896, power_factor_4__3908, power_factor__387 ¦ DC Voltage: dc_pos_voltage__248 (used), dc_voltage__630, dc_pos_voltage__248, dc_pos_voltage__376, dc_voltage_mod1__3852, dc_voltage_mod2__3853, dc_voltage_mod3__3854, dc_voltage_mod4__3855, battery_pack_voltage__1363, control_module_voltage__1371, control_module_voltage__1376, das_battery_voltage__1369, dcdc_1_voltage__1364, dcdc_2_voltage__1365, hvps_1-1_vactual__1386, hvps_1-1_vtarget__1385, hvps_1-2_vactual__1390, hvps_1-2_vtarget__1389, hvps_1-3_vactual__1394, hvps_1-3_vtarget__1393, hvps_2-1_vactual__1398, hvps_2-1_vtarget__1397, hvps_2-2_vactual__1402, hvps_2-2_vtarget__1401, hvps_2-3_vactual__1406, hvps_2-3_vtarget__1405 ¦ DC Current: dc_pos_current__249 (used), dc_current__631, dc_pos_current__249, dc_pos_current__377, dc_current_mod1__3856, dc_current_mod2__3857, dc_current_mod3__3858, dc_current_mod4__3859, hvps_1-1_current__1387, hvps_1-2_current__1391, hvps_1-3_current__1395, hvps_2-1_current__1399, hvps_2-2_current__1403, hvps_2-3_current__1407 ¦ Irradiance: poa_irradiance__245, poa_irradiance__373, poa_irradiance_1__627, poa_irradiance_2__658, poa_10deg_mod3__3846, poa_25deg_mod2__3845, poa_40deg30deg_mod4__3847, poa_40deg_mod1__3844 ¦ Module temperature: module_temp_2__254 (used), module_temp_1__253, module_temp_1__381, module_temp_2__254, module_temp_2__382, module_temp_3__255, module_temp_3__383, module_temp_4__257, module_temp_5__258, module_temp_6__259, module_temp_7__260, mod1_temperatue__3860, mod2_temperature__3861, mod3_temperature__3862, mod4_temperature__3863, module10nw_temp__640, module1sw_temp__659, module3_temp__639, module5se_temp__660, module6ne_temp__641, module8_temp_bot__637, module8_temp_mid__636, module8_temp_top__635, reflector_temp_1__638 | YOY | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=dc_pos_voltage__248 ¦ DC Current=dc_pos_current__249 ¦ Module temperature=module_temp_2__254 | No degradation rate (stopped at 'filter'): Only 1 row(s) survived filtering (need >= 20) -- not enough clean data to estimate degradation. Correctly refused rather than guessing.
my_88_csv_1319.csv | 5.322 | 0 | 0.0% retained (1/3393 rows) |  |  |  | Irradiance | DC Power: computed_dc_power (used), dc_power__583, dc_power__246, power_factor__596 ¦ DC Voltage: dc_pos_voltage__585 (used), dc_pos_voltage__585, dc_pos_voltage__248 ¦ DC Current: dc_pos_current__586 (used), dc_pos_current__586, dc_pos_current__249 ¦ Irradiance: poa_irradiance__582, poa_irradiance__245 ¦ Module temperature: module_temp_1__590 (used), module_temp_1__590, module_temp_1__253, module_temp_2__591 | YOY | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=dc_pos_voltage__585 ¦ DC Current=dc_pos_current__586 ¦ Module temperature=module_temp_1__590 | No degradation rate (stopped at 'filter'): Only 1 row(s) survived filtering (need >= 20) -- not enough clean data to estimate degradation. Correctly refused rather than guessing.
my_89_csv_1320.csv | 0.225 | 328.2 |  |  |  |  | Irradiance | DC Power: computed_dc_power (used), dc_power__422, dc_power__389, dc_power__246, dc_power__628, power_factor__3653, dc_power__374, power_factor__387, dc_power__664, dc_power_mod1__3848, dc_power_mod2__3849, dc_power_mod3__3850, dc_power_mod4__3851, power_factor_1__3872, power_factor_2__3884, power_factor_3__3896, power_factor_4__3908, dc_power__400, dc_power__4025, dc_power__1132, inv1_dc_power__1130, inv2_dc_power__1131, dc_power__564, dc_power__406, dc_power1__4979, dc_power1__5014, dc_power2__4983, dc_power2__5015, dc_power3__4987, dc_power3__5016, dc_power4__4991, dc_power4__5017, tracker_power__4389 ¦ DC Voltage: dc_pos_voltage__424 (used), dc_pos_voltage__424, dc_pos_voltage__391, dc_voltage__630 ¦ DC Current: dc_pos_current__425 (used), dc_pos_current__425, dc_pos_current__392, dc_current__631 ¦ Irradiance: poa_irradiance__421, poa_irradiance__388, poa_irradiance__245, poa_irradiance_1__627, poa_irradiance_2__658, intsolirrad__16, licor1_irradiance__3605, licor2_irradiance__3606, licor3_irradiance__3607, licor4_irradiance__3608, licor5_irradiance__3609, poa_irradiance__3604, referencemodule1_irradiance__3610, referencemodule2_irradiance__3612, poa_irradiance__373, poa_10deg_mod3__3846, poa_25deg_mod2__3845, poa_40deg30deg_mod4__3847, poa_40deg_mod1__3844, poa_irradiance__663, poa_irradiance__399, poa_irradiance__4022, poa_irradiance__4936, poa_irradiance__563, poa_irradiance__405, backofmodule_irradiance__5005, poa_irradiance__5004, refcell1_irrad__4971, refcell2_irrad__4972 ¦ Module temperature: module_temp_1__429 (used), module_temp_1__429, module_temp_1__396, module_temp_2__397 |  | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=dc_pos_voltage__424 ¦ DC Current=dc_pos_current__425 ¦ Module temperature=module_temp_1__429 | No filtering result and degradation rate (stopped at 'duration'): Only ~3 months (<1 year). Degradation correctly not attempted.
my_90_csv_1321.csv | 5.347 | 2935.5 | 75.5% retained (2596/3440 rows) | 2.0683 | no | the computed rate (+2.1%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: whtotal__303 (used), vatotal__302, whtotal__303 | YOY | Time=measured_on ¦ DC Power=whtotal__303
my_91_csv_1322.csv | 0.003 | -3526056.1 |  |  |  |  | Irradiance, Module temperature | DC Power: whtotal__276 (used), whtotal__276 ¦ DC Voltage: vatotal__275 (used), vatotal__275 |  | Time=measured_on ¦ DC Power=whtotal__276 ¦ DC Voltage=vatotal__275 ¦ DC Current=computed_dc_current | No filtering result and degradation rate (stopped at 'duration'): Only ~0 months (<1 year). Degradation correctly not attempted.
my_92_csv_1323.csv | 4.611 | 197.3 | 35.1% retained (1220/3473 rows) | 5.074 | no | the computed rate (+5.1%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: rtw__3600 (used), rtw__3600 | YOY | Time=measured_on ¦ DC Power=rtw__3600
my_93_csv_1324.csv | 2.453 | 699.8 | 85.1% retained (3024/3552 rows) | 66.5829 | no | the computed rate (+66.6%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance, Module temperature | DC Power: whtotal__279 (used), whtotal__279 ¦ DC Voltage: vatotal__278 (used), vatotal__278 | YOY | Time=measured_on ¦ DC Power=whtotal__279 ¦ DC Voltage=vatotal__278 ¦ DC Current=computed_dc_current
my_94_csv_1325.csv | 5.254 | 137611.7 | 1.3% retained (45/3473 rows) | 41.0757 | no | the computed rate (+41.1%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr); the year-over-year changes disagree with each other by about ±9.1%/yr — too scattered for this single number to be trusted | Module temperature | DC Power: whtotal__282 (used), whtotal__282 ¦ DC Voltage: vatotal__281 (used), vatotal__281 ¦ Irradiance: rtw__280 (used), rtw__280 | YOY (energy-ratio) | Time=measured_on ¦ DC Power=whtotal__282 ¦ DC Voltage=vatotal__281 ¦ DC Current=computed_dc_current ¦ Irradiance=rtw__280
my_95_csv_1326.csv | 3.622 | 48116.3 | 89.0% retained (3186/3581 rows) | 32.8512 | no | the computed rate (+32.9%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: whtotal__285 (used), vatotal__284, whtotal__285 | YOY | Time=measured_on ¦ DC Power=whtotal__285
my_96_csv_1328.csv | 0.468 | 2138.9 |  |  |  |  | Irradiance, Module temperature | DC Power: whtotal__291 (used), whtotal__291 ¦ DC Voltage: vatotal__290 (used), vatotal__290 |  | Time=measured_on ¦ DC Power=whtotal__291 ¦ DC Voltage=vatotal__290 ¦ DC Current=computed_dc_current | No filtering result and degradation rate (stopped at 'duration'): Only ~6 months (<1 year). Degradation correctly not attempted.
my_97_csv_1329.csv | 5.232 | 138770.1 | 85.6% retained (2935/3430 rows) | 16.237 | no | the computed rate (+16.2%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance, Module temperature | DC Power: whtotal__294 (used), whtotal__294 ¦ DC Voltage: vatotal__293 (used), vatotal__293 | YOY | Time=measured_on ¦ DC Power=whtotal__294 ¦ DC Voltage=vatotal__293 ¦ DC Current=computed_dc_current
my_98_csv_1330.csv | 0.512 | 198.5 |  |  |  |  | DC Voltage, DC Current, Irradiance, Module temperature | DC Power: vatotal__296 (used), vatotal__296, whtotal__297 |  | Time=measured_on ¦ DC Power=vatotal__296 | No filtering result and degradation rate (stopped at 'duration'): Only ~6 months (<1 year). Degradation correctly not attempted.
my_99_csv_1331.csv | 1.344 | 33 | 0.0% retained (1/3541 rows) |  |  |  | Irradiance | DC Power: computed_dc_power (used), dc_power__246, dc_power__400, dc_power__1132, power_factor__3653, inv1_dc_power__1130, inv2_dc_power__1131, dc_power__583, power_factor__596, dc_power__1084, dc_power__374, power_factor__1097, power_factor__387, dc_power__628 ¦ DC Voltage: dc_pos_voltage__248 (used), dc_pos_voltage__248, inv1_string1_dc_voltage__3627, inv1_string2_dc_voltage__3628 ¦ DC Current: dc_pos_current__249 (used), dc_pos_current__249, inv1_string1_dc_current__3614, inv1_string2_dc_current__3615 ¦ Irradiance: poa_irradiance__245, poa_irradiance__3604, poa_irradiance__399, licor1_irradiance__3605, licor2_irradiance__3606, licor3_irradiance__3607, licor4_irradiance__3608, licor5_irradiance__3609, referencemodule1_irradiance__3610, referencemodule2_irradiance__3612, poa_irradiance__582, poa_irradiance__1083, poa_irradiance__373, poa_irradiance_1__627, poa_irradiance_2__658 ¦ Module temperature: module_temp_2__254 (used), module_temp_1__253, module_temp_2__254, module_temp_3__255 | LR | Time=measured_on ¦ DC Power=computed_dc_power ¦ DC Voltage=dc_pos_voltage__248 ¦ DC Current=dc_pos_current__249 ¦ Module temperature=module_temp_2__254 | No degradation rate (stopped at 'filter'): Only 1 row(s) survived filtering (need >= 20) -- not enough clean data to estimate degradation. Correctly refused rather than guessing.
new_manifest.csv | [6 empty] | Time, DC Power, DC Voltage, DC Current, Irradiance, Module temperature | none |  |  | No filtering result and degradation rate (stopped at 'analyze'): Not enough information: no usable PV variables could be identified in this dataset.
new_my_1.csv | 16.945 | 1 | 26.5% retained (39014/147394 rows) | -1.9897 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_10.csv | 16.003 | 1 | 22.0% retained (30626/139192 rows) | -0.8969 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_11.csv | 16.003 | 0.8 | 16.3% retained (22644/139192 rows) | -0.7968 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_12.csv | 16.003 | 0.7 | 12.9% retained (17919/139192 rows) | -2.6446 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_13.csv | 15.685 | 0.9 | 24.6% retained (33503/136377 rows) | -1.3639 | yes |  | DC Voltage, Module temperature | DC Power: Active_Power (used), Active_Power ¦ DC Current: Current_Phase_Average (used), Current_Phase_Average ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Radiation_Global_Tilted, Diffuse_Horizontal_Radiation, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ DC Current=Current_Phase_Average ¦ Irradiance=Global_Horizontal_Radiation
new_my_14.csv | 17.437 | 3.2 | 23.5% retained (35639/151728 rows) | -2.6239 | yes |  | DC Voltage, Module temperature | DC Power: Active_Power (used), Active_Power ¦ DC Current: Current_Phase_Average (used), Current_Phase_Average ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Radiation_Global_Tilted, Diffuse_Horizontal_Radiation, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ DC Current=Current_Phase_Average ¦ Irradiance=Global_Horizontal_Radiation
new_my_15.csv | 16.945 | 1.2 | 23.8% retained (35070/147396 rows) | -1.5462 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_16.csv | 12.077 | 4.3 | 27.1% retained (28402/104761 rows) | -4.9294 | no | the computed rate (-4.9%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | DC Voltage, Module temperature | DC Power: Active_Power (used), Active_Power ¦ DC Current: Current_Phase_Average (used), Current_Phase_Average ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Radiation_Global_Tilted, Diffuse_Horizontal_Radiation, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ DC Current=Current_Phase_Average ¦ Irradiance=Global_Horizontal_Radiation
new_my_17.csv | 16.977 | 1.2 | 26.8% retained (39570/147689 rows) | -0.7984 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_18.csv | 16.977 | 1.2 | 25.6% retained (37880/147689 rows) | -1.5854 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_2.csv | 16.003 | 0.9 | 20.3% retained (28237/139192 rows) | -0.9163 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_3.csv | 7.389 | 1.2 | 18.8% retained (12177/64760 rows) | -1.2367 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_4.csv | 12.057 | 1.3 | 27.2% retained (28471/104623 rows) | -0.6434 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_5.csv | 15.54 | 1 | 21.0% retained (28429/135154 rows) | -0.5711 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_6.csv | 7.389 | 1.2 | 16.0% retained (10381/64760 rows) | -0.2051 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_7.csv | 16.003 | 0.7 | 16.3% retained (22720/139192 rows) | -0.8109 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_8.csv | 15.54 | 0.5 | 10.8% retained (14631/135154 rows) | -1.1078 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted, Radiation_Diffuse_Tilted | YOY | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
new_my_9.csv | 16.003 | 1.2 | 26.4% retained (36687/139192 rows) | -1.052 | yes |  | DC Voltage, DC Current, Module temperature | DC Power: Active_Power (used), Active_Power ¦ Irradiance: Global_Horizontal_Radiation (used), Global_Horizontal_Radiation, Diffuse_Horizontal_Radiation, Radiation_Global_Tilted | YOY (energy-ratio) | Time=timestamp ¦ DC Power=Active_Power ¦ Irradiance=Global_Horizontal_Radiation
system_10__date_2000_05_10.csv | 0 | 19.2 |  |  |  |  | none | DC Power: dc_power__422 (used), dc_power__422 ¦ DC Voltage: dc_pos_voltage__424 (used), dc_pos_voltage__424 ¦ DC Current: dc_pos_current__425 (used), dc_pos_current__425 ¦ Irradiance: poa_irradiance__421 (used), poa_irradiance__421 ¦ Module temperature: module_temp_1__429 (used), module_temp_1__429, module_temp_2__430, module_temp_3__431 |  | Time=measured_on ¦ DC Power=dc_power__422 ¦ DC Voltage=dc_pos_voltage__424 ¦ DC Current=dc_pos_current__425 ¦ Irradiance=poa_irradiance__421 ¦ Module temperature=module_temp_1__429 | No filtering result and degradation rate (stopped at 'duration'): Only ~0 months (<1 year). Degradation correctly not attempted.
under2yr_01.csv | 1.292 | 11820.2 | 40.4% retained (580/1435 rows) | 10.0715 | no | the data spans only 1.3 year(s) — under 2 years is too short to separate real aging from seasonal weather; the computed rate (+10.1%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance, Module temperature | DC Power: dc_power__3093 (used), dc_power__3093 ¦ DC Voltage: inv1_dc_voltage__3095 (used), inv1_dc_voltage__3095 ¦ DC Current: inv1_dc_current__3096 (used), inv1_dc_current__3096 | LR | Time=measured_on ¦ DC Power=dc_power__3093 ¦ DC Voltage=inv1_dc_voltage__3095 ¦ DC Current=inv1_dc_current__3096
under2yr_02.csv | 1.292 | 44291.1 | 39.9% retained (572/1435 rows) | 11.1015 | no | the data spans only 1.3 year(s) — under 2 years is too short to separate real aging from seasonal weather; the computed rate (+11.1%/yr) is outside the physically plausible range (real degradation is roughly 0 to −3%/yr) | Irradiance, Module temperature | DC Power: dc_power__3126 (used), dc_power__3126 ¦ DC Voltage: inv1_dc_voltage__3130 (used), inv1_dc_voltage__3130 ¦ DC Current: inv1_dc_current__3131 (used), inv1_dc_current__3131 | LR | Time=measured_on ¦ DC Power=dc_power__3126 ¦ DC Voltage=inv1_dc_voltage__3130 ¦ DC Current=inv1_dc_current__3131